## Temp JC PID
PID Set 1 |  |  | PID Set 1
620A TC/TC
TYPE T | PID set 1 | Channel 1 |  | Channel 2
|  | INC (HEAT) | DEC (COOL) | INC (HEAT) | INC(COOL)
| CYCLE TIME (SEC) | 2 | 2 | 2 | 2
| BW (Prop Band) | 366.7 | 366.7 | 8.3 | 9.4
| PG (prop Gain) | 0.3 | 0.3 | 13.3 | 11.7
| AUTO_RESET (INTEGRAL) | 2 | 2 | 0 | 0
| RWI % (reset without inhibit) | 100 | 100 | 100 | 100
| Unwind Factor | 2 | 2 | 2 | 2
| Reset_Clip % | 0 | 0 | 0 | 0
| Rate (Derivativel) | 0 | 0 | 0 | 0
| ID Band | 0 | 0 | 0 | 0
| Minimum Output Pwr % | 0 | 0 | 0 | 0
| Maximum Output Pwr % | 100 | 100 | 100 | 100
PID Set 2
| PID set 2 | Channel 1 |  | Channel 2
|  | INC (HEAT) | DEC (COOL) | INC (HEAT) | INC (COOL)
| Cycl Time (sec) | 2 | 2 | 2 | 2
| BW (PROP BAND) | 110 | 110 | 2.7 | 2.7
| PROP (GAIN) | 1.8 | 1.8 | 41.4 | 41.4
| AUTO_RESET (INTEGRAL) | 0 | 0 | 0 | 0
| RWI % (Reset witout inhibit) | 100 | 100 | 100 | 100
| Unwind Factor | 0 | 0 | 0 | 0
| Reset_clip % | 0 | 0 | 0 | 0
| Rate (Derivativel) | 0 | 0 | 0 | 0
| ID Band | 0 | 0 | 0 | 0
| Minimum Output Pwr % | 0 | 0 | 0 | 0
| Maximum Output Pwr % | 100 | 100 | 100 | 100

## Temp JC Setup
Item # | Information | Configuration | Hanse 620A
0 | 600a/620a Prom Version | 229 | Temp/Temp
1 | Ch1 Units | Degrees-C
2 | Ch 1 inputs config. | T
3 | Ch 1 hi span limit valve | 225
4 | Ch 1 lo span limit valve | -125
5 | Ch 1 Current loop assigined to: | CH 2
6 | Ch 1 Cur_lp valve 4-20, 0-16 | 4-20ma
7 | Ch 1 current loop action (Heat,Cool) | Dual
8 | Ch 1input low-pass filter time concent | 2
9 | Ch 2 units | Degrees-C
10 | Ch 2 Inputs config. | T
11 | Ch 2 Hi-span Limit Valve | 225
12 | Ch 2 Lo-span limit Valve | -125
13 | Ch 2 Current Loop assigined To: | CH 2
14 | Ch 2 Cur_IP valve 4-20, 0=16 | 4-20ma
15 | Ch 2 Current Loop Action 9Heat, Cool) | Heat
16 | Ch 2 Input Low_pass Filter Time conncent | 0.8
17 | Programer Mode | FAST TRAC
18 | FAST TRAC Lo Limit | -125
19 | FAST TRAC HI Limit | 225
20 | Ch 1 Limits assigned To: | Ch 2 pv
21 | Ch 1 HI Process Limit | 250
22 | Ch 1 Lo Process Limit | 20
23 | CH 2 Limits assigned to: | CH 1 sp
24 | CH 2 Hi process Limit | 250
25 | Ch2 Lo process limit | 0
26 | Sychrenizer (1=on, 0=Off) | 0
27 | On Inputs #8 | NO_ACTION
28 | Input #8 Program Number to run | 98
29 | Input #8 Starting step | 1
30 | Pwr Fail Mode | NO_ACTION
31 | Pwr Fail Ch 1 Limits | OFF
32 | Pwr fail Prgm # run | 99
33 | Pwr fail Startin step | 1
34 | Pwr fail Ch 2 Limits | Off
35 | WB/DB Site Elev. (in Ft) | 0

## Vib-RH PID
PID Set
620A/600A
Vibration/RH
| Pset 1 | Channel 1 |  | Channel 2
CH 1 = 0-1vdc |  | Inc (Heat) | Dec(Cool) | Inc(Heat) | Dec(Cool)
Ch 2 =4-20ma | Cycle time (sec) | 2 | 2 | 4 | 4
| BW (Prop hand) | 1100 | 1100 | 20 | 20
| PG prop gain | 0.1 | 0.1 | 5.5 | 5.5
| Auto_Reset (Intergal) | 50 | 50 | 0.32 | 0.32
| RWI% (reset without inhibit) | 100 | 100 | 10 | 10
| Unwind_Factor | 0 | 0 | 0 | 0
| Reset Clip% | 0 | 0 | 0 | 0
| Rate (derivative) | 0 | 0 | 0 | 0
| ID Band | 0 | 0 | 0 | 0
| Mininum Output Pwr (%) | 0 | 0 | 0 | 0
| Maximum output Pwr (%) | 100 | 100 | 100 | 100
| Pset 2 | Channel 1 |  | Channel 2
|  | Inc (Heat) | Dec(Cool) | Inc (Heat) | Dec (Cool)
| Cycle time (sec) | 2 | 2 | 2 | 2
| BW (Prop hand) | 2.7 | 2.7 | 2.7 | 2.7
| PG prop gain | 41.4 | 41.4 | 41.4 | 41.4
| Auto_Reset (Intergal) | 0 | 0 | 0 | 0
| RWI% (reset without inhibit) | 100 | 100 | 100 | 100
| Unwind_Factor | 0 | 0 | 0 | 0
| Reset Clip% | 0 | 0 | 0 | 0
| Rate (derivative) | 0 | 0 | 0 | 0
| ID Band | 0 | 0 | 0 | 0
| Mininum Output Pwr (%) | 0 | 0 | 0 | 0
| Maximum output Pwr (%) | 100 | 100 | 100 | 100

## Vib-RH Setup
Item # | Information | Configuration
0 | 600a/620a Prom version | 229
1 | Ch1 units | Linear | Hanse 620a/600a
2 | Ch 1 Input cinfg. | Linear - mv | Vib/RH
3 | Ch1 hi span limit value | 105
4 | Ch1 Lo Span limit value | -5
5 | Ch1 current loop assigined to: | CH 1
6 | Ch1 Cur_Ip value 4-20, 0-16 | 2001-04-20
7 | Ch1 current loop action (heat, cool) | HEAT
8 | Ch1 input Low-pass filter time constant | 0
9 | Ch2 units | Linear
10 | Ch2 input config | I
11 | ch2 Hi span Limit value | 105
12 | Ch2 Lo span limit value | -5
13 | Ch2 Current loop assigined to: | CH2
14 | Ch2 Cur_ip value(4-20,0-16) | 4-20ma
15 | Ch2 current Loop action (heat,cool) | HEAT
16 | Ch2 Input low-pass filter time constant | 2
17 | Programer Mode | DUAL
18 | FastTRACK lo limit | 150
19 | FastTRACK Hi limit | 250
20 | Ch1 limits assigined to: | 1 Ch1pv
21 | Ch1 Hi process limit | 315
22 | Ch1 Lo Process limit | -100
23 | Ch2 Limits Assigined to: | s Ch 1 sp
24 | Ch2 hi process limit | 1
25 | Ch2 lo process limit | 0
26 | Sychrenizer (1=on, 0=Off) | 0
27 | ON INPUT #8 | DISABLE
28 | Input #8 program number to run | 98
29 | Input #8 starting step | 1
30 | Pwr fail mode | No_action
31 | Pwr Fail Ch1 limits | OFF
32 | Pwr fail Program# to run | 99
33 | Pwr Failstartin step | 1
34 | Pwr fail Ch2 limits | OFF
35 | WB/DB Site elev. (in feet) | 0